ISO/CD XXXXX

Date: 202X-XX-XX

ISO/TC XXX/WG XX

Secretariat: XXX

Intelligent regulation and control systems for water networks — Technical requirements

Systèmes de régulation et de contrôle intelligents des réseaux d’eau — Exigences techniques

Warning for WDs and CDs: This document is not an ISO International Standard. It is distributed for review and comment. It is subject to change without notice and may not be referred to as an International Standard.

# Contents

Foreword

Introduction

1   Scope

2   Normative references

3   Terms and definitions

4   Abbreviated terms

5   General requirements

6   Autonomy levels for water network operations

7   Operational design domain (ODD)

8   Multi-network coordinated security

9   Water network common information model (Water-CIM)

10  Interoperability protocol stack

11  Scenario-based testing and verification

12  Engineering acceptance

13  Version management and continuous compliance

Annex A (informative) Comparison with SAE J3016 driving automation levels

Annex B (informative) Protocol selection decision matrix

Bibliography

# Foreword

ISO (the International Organization for Standardization) is a worldwide federation of national standards bodies (ISO member bodies). The work of preparing International Standards is normally carried out through ISO technical committees.

ISO/CD XXXXX was prepared by Technical Committee ISO/TC XXX, XXXX, Subcommittee SC XX, XXXX.

This document addresses the growing need for standardized technical requirements for intelligent regulation and control systems applied to water networks, including inter-basin water transfer projects, cascade reservoir systems, urban water supply networks, and irrigation canal systems.

This document draws upon established international standards from the automotive sector (SAE J3016, ISO 26262, ISO 21448), industrial automation (IEC 62443, IEC 62541), and water management (ISO 24591), adapting their proven frameworks to the unique characteristics of water network infrastructure.

Any feedback or questions on this document should be directed to the user’s national standards body.

# Introduction

The accelerating construction of national and transnational water networks worldwide demands a transition from traditional manual dispatch to intelligent, autonomous operation. However, the water sector currently faces several critical challenges:

Design-operation disconnect: Requirements expressed in natural language documents are manually translated into control code, leading to widespread “works in simulation, fails in deployment” phenomena.

Floating intelligence: Advanced algorithms remain disconnected from existing SCADA infrastructure, unable to integrate effectively with field PLCs and RTUs.

Model silos: Heterogeneous models (hydrological, hydraulic, control) lack standardized interfaces for runtime coupling.

OT/IT security conflicts: Physical isolation between operational technology (OT) control networks and information technology (IT) enterprise networks prevents distributed agents from coordinated operation.

No acceptance criteria: Engineering acceptance of intelligent control systems lacks quantitative admission conditions.

No autonomy classification: The water sector has not established an autonomy level framework analogous to SAE J3016 in the automotive industry.

This document establishes a comprehensive technical framework addressing these gaps. It introduces model-based design (MBD) as the core engineering paradigm, defines a six-level autonomy classification (L0–L5) for water network operations, specifies the integration architecture between legacy SCADA systems and multi-agent systems (MAS), and provides quantitative engineering acceptance criteria.

The document is structured around the concept that MAS serves as a “distributed software-defined supervisory layer” deployed across edge gateways and cloud containers, operating in coordination with existing SCADA infrastructure rather than replacing it. This “SCADA (body) + MAS (brain)” dual-layer architecture respects the installed base of industrial control assets while enabling progressive advancement toward autonomous operations.

# 1   Scope

This document specifies technical requirements for intelligent regulation and control systems for water networks, including requirements for:

terms and definitions;

autonomy levels for water network operations;

operational design domain (ODD);

model-based design (MBD) paradigm;

SCADA and multi-agent system (MAS) integration architecture;

multi-network coordinated security between OT and IT domains;

water network common information model (Water-CIM);

interoperability protocol stack (distinguishing computation interfaces from communication buses);

scenario-based testing and verification;

engineering acceptance;

version management and continuous compliance.

This document is applicable to the design, development, testing, acceptance, and operation of intelligent regulation and control systems for the following water network types:

national water networks and their sub-networks;

inter-basin water transfer projects;

cascade reservoir group joint dispatch systems;

urban water supply network control systems;

irrigation district canal distribution systems.

This document does not apply to local automation of individual gate stations or pump stations at the PLC level. However, when such local control systems serve as the execution layer of a water network control system, their interfaces shall conform to the relevant provisions of this document.

# 2   Normative references

The following documents are referred to in the text in such a way that some or all of their content constitutes requirements of this document. For dated references, only the edition cited applies. For undated references, the latest edition of the referenced document (including any amendments) applies.

IEC 61131-3, Programmable controllers — Part 3: Programming languages

IEC 61970 (all parts), Energy management system application program interface (EMS-API) — Common information model (CIM)

IEC 62443 (all parts), Security for industrial automation and control systems

IEC 62541 (all parts), OPC Unified Architecture

ISO 24591 (all parts), Smart water management

ISO 26262 (all parts), Road vehicles — Functional safety

ISO 21448, Road vehicles — Safety of the intended functionality (SOTIF)

SAE J3016, Taxonomy and definitions for terms related to driving automation systems for on-road motor vehicles

OMG Data Distribution Service (DDS), Version 1.4

OGC 14-068, OpenMI 2.0 — Open Modelling Interface Standard

OGC WaterML 2.0 — Part 1: Timeseries, and Part 2: Ratings, Gaugings and Sections

FMI 3.0, Functional Mock-up Interface Standard

# 3   Terms and definitions

For the purposes of this document, the following terms and definitions apply.

ISO and IEC maintain terminology databases for use in standardization at the following addresses:

ISO Online browsing platform: available at https://www.iso.org/obp

IEC Electropedia: available at https://www.electropedia.org/

## 3.1

water network

ensemble of water sources, conveyance infrastructure, reservoirs, gate stations, pump stations, pipelines, and their interconnection relationships, together with the corresponding information network

## 3.2

intelligent regulation and control

process of achieving intelligent operation of water resource dispatch, hydraulic structure control, and safety supervision within a water network through digital twin, artificial intelligence, and control theory technologies

## 3.3

autonomous operation

capability state in which a water network regulation and control system can complete safe and reliable operation within its operational design domain with no or minimal human intervention

## 3.4

cyber-physical-social system; CPSS

complex system architecture integrating interactions across cyberspace, physical space, and social space, where physical space refers to hydraulic structures and water flow processes, and social space refers to water demand, dispatch regulations, and management decisions

## 3.5

digital twin

virtual representation of a water network physical entity, synchronized through real-time data and driven by physical models, enabling mirroring, prediction, and optimization of the physical system state

## 3.6

supervisory control and data acquisition system; SCADA

industrial automation system responsible for field data acquisition, supervisory monitoring, and basic control, including PLCs/RTUs, communication networks, and supervisory software

NOTE   In this document, SCADA is defined as the “foundation layer” of the intelligent control system, responsible for hard interlock protection and serving as the last line of defence. SCADA retains the right to override any instruction from the MAS layer that violates hard constraints.

## 3.7

multi-agent system; MAS

distributed control software cluster comprising multiple autonomous agents working cooperatively

NOTE   In this document, MAS is defined as a “distributed software-defined supervisory layer” deployed on edge gateways or cloud containers, effectively assuming the logical control authority of traditional supervisory stations.

## 3.8

edge agent

agent instance deployed on a field edge gateway or industrial server, operating within the OT control network, responsible for real-time closed-loop control of a single station or local water network segment

## 3.9

area agent

agent instance deployed at the management office level, responsible for distributed model predictive control (DMPC) coordination among multiple edge agents within a regional scope

## 3.10

cloud agent

agent instance deployed in the cloud, operating within the IT enterprise network, responsible for global economic dispatch, long-cycle optimization, and digital twin maintenance

NOTE   Cloud agents shall not issue direct control commands; they shall only provide dispatch recommendations.

## 3.11

OT network; operational technology network

physically isolated industrial control network carrying SCADA system and edge agent communications, strictly prohibited from connecting to the internet

## 3.12

IT network; information technology network

enterprise network carrying cloud agents, digital twin platforms, and management information systems, which may connect to the internet to obtain meteorological, energy pricing, and other external data

## 3.13

model-based design; MBD

engineering paradigm using mathematical models as the single source of truth throughout the entire lifecycle, encompassing requirements definition, algorithm design, code generation, and test verification

NOTE   The core principles of MBD are: the model is truth, code is auto-generated, and testing is continuous.

## 3.14

operational design domain; ODD

specific set of conditions under which an intelligent regulation and control system is designed to operate normally, including but not limited to hydraulic boundary conditions, meteorological conditions, communication state, sensor availability, and downstream demand

NOTE   The ODD shall be defined as a computable mathematical set, not merely described in natural language.

## 3.15

executable specification

system requirements document expressed in the form of computable mathematical models, possessing the capability for simulation execution, automated verification, and automated code generation

## 3.16

model-in-the-loop testing; MIL

testing method that verifies algorithm logic correctness by jointly running the control algorithm model and the controlled plant model in a pure model environment

## 3.17

software-in-the-loop testing; SIL

testing method that jointly tests auto-generated code from a model with the controlled plant model in a software environment, with the core purpose of verifying numerical consistency between the auto-generated code and the source model

## 3.18

hardware-in-the-loop testing; HIL

testing method that deploys control code to real controller hardware and tests jointly with a real-time simulation model of the controlled plant, with the core purpose of verifying real-time performance, communication reliability, and failover capability under real hardware conditions

## 3.19

safety case

structured argument document used to demonstrate that a system is sufficiently safe in its operational environment, typically organized using Goal Structuring Notation (GSN) or Claims-Arguments-Evidence (CAE) framework

## 3.20

manual operation (L0)

operational state in which all regulation and control decisions and execution are performed by humans, with the system providing only basic data acquisition and display functions

## 3.21

assisted operation (L1)

operational state in which the system can analyse data and provide regulation recommendations under specific conditions, but all final decisions and execution remain the responsibility of human operators

## 3.22

partial automation (L2)

operational state in which, within a limited ODD, the system can automatically execute routine regulation tasks, while humans shall continuously supervise system operation and be prepared to take over at any time

NOTE   Humans remain the ultimate safety responsible entity at L2.

## 3.23

conditional autonomy (L3)

operational state in which, within a clearly defined ODD, the system can autonomously complete the full regulation closed loop from perception through decision to execution, with human intervention only when the system issues a takeover request

NOTE   L3 represents the critical watershed for human-machine responsibility transfer.

## 3.24

high autonomy (L4)

operational state in which, within an extended ODD, the system can autonomously handle regulation tasks including multiple types of abnormal conditions, with autonomous fault identification, degradation, and recovery capabilities

## 3.25

full autonomy (L5)

operational state in which the system can operate fully autonomously under all foreseeable conditions without any human intervention

NOTE   L5 is a long-term vision goal; current technology does not support engineering implementation.

## 3.26

model coupling

technical process of enabling two or more heterogeneous models to work cooperatively through standardized interfaces with runtime data exchange

## 3.27

functional mock-up unit; FMU

model unit packaged in compliance with the FMI standard, containing a model description file and executable code, supporting cross-platform exchange and co-simulation

## 3.28

water network common information model; Water-CIM

unified semantic model for water network assets, topology, measurements, control logic, and agents, based on the IEC 61970 CIM architecture and reconstructed for water network characteristics

## 3.29

data distribution service; DDS

decentralized publish/subscribe middleware protocol with peer-to-peer node connectivity and QoS contracts (e.g., DEADLINE, RELIABILITY), suitable as a real-time communication bus for distributed agent coordination

## 3.30

set-point driven paradigm

operational paradigm in which MAS does not directly operate SCADA digital outputs (DO) but instead issues only target set-point values via OPC UA, with the SCADA layer responsible for actuator driving and safety verification

## 3.31

hard constraint

absolute safety boundary that shall not be violated during system operation, such as maximum warning water level, maximum allowable flow rate, or minimum ecological base flow

NOTE   Violation of a hard constraint shall trigger emergency shutdown or automatic degradation.

## 3.32

soft constraint

optimization objective for system operation that may be relaxed or adjusted under specific conditions, such as target water level, economic dispatch objective, or power generation maximization target

## 3.33

circuit breaker

protection mechanism that automatically disconnects a fault path and degrades to a safe fallback strategy when the control system detects an abnormal state

NOTE   Typical trigger conditions include model numerical divergence, sensor failure, communication interruption, and MAS heartbeat timeout.

## 3.34

island autonomy mode

emergency operating mode in which an edge agent, upon detecting interruption of the communication link with the cloud, automatically switches to operating solely based on local objectives and local sensor data, without waiting for cloud instructions

## 3.35

engineering acceptance package

collection of documents that shall be submitted during engineering acceptance of an intelligent regulation and control system, including the ODD declaration, XIL test reports, safety case, distributed deployment topology file, multi-network security policy set, and disconnection autonomy test report

# 4   Abbreviated terms

For the purposes of this document, the following abbreviated terms apply.

| Abbreviated term | Full term |
| --- | --- |
| BMI | Basic Model Interface |
| CAE | Claims-Arguments-Evidence |
| CIM | Common Information Model |
| CPSS | Cyber-Physical-Social System |
| DDS | Data Distribution Service |
| DDT | Distributed Deployment Topology |
| DMPC | Distributed Model Predictive Control |
| DMZ | Demilitarized Zone |
| FMI | Functional Mock-up Interface |
| FMU | Functional Mock-up Unit |
| GSN | Goal Structuring Notation |
| HIL | Hardware-in-the-Loop |
| IaC | Infrastructure as Code |
| IT | Information Technology |
| MAS | Multi-Agent System |
| MBD | Model-Based Design |
| MIL | Model-in-the-Loop |
| MPC | Model Predictive Control |
| ODD | Operational Design Domain |
| OPC UA | OPC Unified Architecture |
| OT | Operational Technology |
| OTA | Over-the-Air |
| QoS | Quality of Service |
| SIL | Software-in-the-Loop |
| SOTIF | Safety of the Intended Functionality |
| XIL | X-in-the-Loop (collective term for MIL, SIL, and HIL) |

# 5   General requirements

## 5.1   System architecture

The water network intelligent regulation and control system shall adopt a “SCADA (foundation layer) + MAS (intelligence layer)” dual-layer integration architecture. SCADA serves as the system’s actuator layer, responsible for data acquisition, hard interlock protection, and actuator driving. MAS serves as the cognitive decision layer in the form of a distributed software-defined supervisory system, responsible for state reconstruction, optimization, and coordinated control. The two layers shall communicate through standardized interfaces, forming a “dual-layer, dual-speed” operating mode.

The system shall be organized into three hierarchical tiers, as specified in Table 1.

Table 1 — System architecture tiers

| Tier | Name | Deployment | Responsibilities and requirements |
| --- | --- | --- | --- |
| L0 | Local control tier (SCADA/PLC) | Field PLC cabinets | Millisecond-level data acquisition, single-point PID control, electrical protection, hard interlock protection. Compliant with IEC 61131-3. SCADA retains veto authority — any instruction violating hard constraints shall be physically intercepted |
| L1 | Regional control tier (Edge/Area MAS) | Edge gateways / office servers | Edge agents: single-station real-time closed-loop control. Area agents: regional DMPC coordination. Deployed on OT network. Control cycle: minutes to hours |
| L2 | Global dispatch tier (Cloud MAS) | Cloud containers | Network-wide resource optimization and long-cycle dispatch. Deployed on IT network. Cycle: days to months. Cloud agents shall not issue direct control commands — only dispatch recommendations |

The interaction rules between tiers shall satisfy the following requirements:

upper tiers shall issue control targets (set-points) to lower tiers, and lower tiers shall provide operational state feedback to upper tiers;

each tier shall possess independent safety degradation capability; when upper-tier communication is interrupted, the lower tier shall autonomously enter a safe state;

the L0 tier (SCADA) shall have ultimate veto authority over MAS instructions; any instruction violating hard constraints shall be intercepted at the SCADA layer.

## 5.2   SCADA and MAS integration interface

SCADA and MAS belong to two heterogeneous domains (OT and IT). OPC UA (IEC 62541) shall be adopted as the integration bridge. The integration interface shall satisfy the following requirements:

Semantic mapping: MAS shall not directly read/write SCADA register addresses. Instead, it shall read/write semanticized object attributes via the OPC UA information model (e.g., Pump_01.Flow.SetPoint). A complete machine-readable mapping table from SCADA tags to Water-CIM objects shall be delivered as part of engineering acceptance.

Set-point driven paradigm: MAS shall not directly operate actuator digital outputs (DO). It shall only issue target set-point values via OPC UA. The SCADA layer shall be responsible for actuator driving and safety verification.

Heartbeat and circuit breaker: MAS shall transmit periodic heartbeat signals to SCADA. If the heartbeat times out (default threshold: 500 ms), SCADA shall automatically revoke MAS control authority and revert to local rule-based control.

Authority levels: The system shall support three levels of control authority — “local manual / edge automatic / cloud advisory” — with local manual always having the highest priority.

## 5.3   Model-based design (MBD) paradigm

Water network control systems with an autonomy level of L2 or above shall adopt the model-based design (MBD) paradigm for developing their core control logic. The MBD paradigm shall satisfy the following requirements:

requirements shall be expressed as executable specifications, including mathematically defined ODDs, formalized constraint conditions, and computable control objectives;

verified control models shall be automatically translated into deployable code through industrial-standard code generators; core control logic shall not be hand-coded;

the same model shall be used throughout MIL, SIL, and HIL testing — the model used during design shall directly serve verification and ultimately generate operational code;

each model shall possess a unique version identifier and strong hash value, ensuring that online operational code is traceable to its source model.

NOTE   L1 systems should adopt the MBD paradigm but this is not mandatory.

## 5.4   Fundamental safety requirements

The water network intelligent regulation and control system shall comply with the following safety principles:

Safety-first principle: Hard constraint protection shall be independent of intelligent control algorithms. SCADA-layer hard interlock protection shall operate independently of MAS.

Fail-safe principle: No single fault (sensor failure, communication interruption, algorithm divergence, MAS crash) shall cause the system to enter an unsafe state.

Observability principle: Critical decision processes shall be recordable, traceable, and explainable. Every MAS control instruction shall have an audit log.

Human takeover principle: Systems at L4 or below shall allow safe human takeover at any time.

# 6   Autonomy levels for water network operations

## 6.1   Level framework

The autonomous operation capability of a water network control system shall be classified into six levels, L0 through L5. The core classification dimension is the allocation of responsibility between humans and machines across the perception–decision–execution chain. The detailed definition of each level is given in Table 2.

Table 2 — Water network autonomy levels

| Level | Name | Perception | Decision | Execution | Fault response | Human role | MAS configuration |
| --- | --- | --- | --- | --- | --- | --- | --- |
| L0 | Manual | Human | Human | Human | Human | Full responsibility | None |
| L1 | Assisted | Human+System | Human | Human | Human | Decision-maker | Cloud advisory |
| L2 | Partial automation | System | System | System | Human | Supervisor | Edge closed-loop |
| L3 | Conditional autonomy | System | System | System | System→Human | Fallback takeover | Edge + Area |
| L4 | High autonomy | System | System | System | System | Exception handler | Full-tier coordination |
| L5 | Full autonomy | System | System | System | System | Not required | Full-tier coordination |

## 6.2   Level determination rules

The autonomy level of a system shall be determined according to the “bucket principle”: the level shall be set by the lowest-performing dimension among perception, decision, execution, and fault response.

EXAMPLE   If decision-making and execution have both achieved automation but fault response still relies on human intervention, the system level shall be determined as L2, not L3.

## 6.3   Level declaration requirements

At system delivery, the constructor shall explicitly declare the system’s autonomy level and provide supporting evidence. The declaration shall include:

the declared autonomy level (L0–L5);

a complete ODD description corresponding to the declared level;

implementation details for each dimension (perception, decision, execution, fault response), including the corresponding MAS deployment configuration;

the degradation strategy when the ODD is exceeded, including the MAS-to-SCADA control authority reversion plan.

# 7   Operational design domain (ODD)

## 7.1   ODD definition requirements

Each intelligent regulation and control system shall clearly define its operational design domain. The ODD shall be defined as a computable mathematical set and shall not be expressed solely in natural language. The ODD shall cover at least the dimensions specified in Table 3.

Table 3 — ODD parameter dimensions

| Dimension | Name | Example parameters |
| --- | --- | --- |
| D1 | Hydraulic boundary | Upstream inflow range, downstream water level range, initial reservoir storage, channel roughness range |
| D2 | Meteorology and environment | Temperature range, rainfall intensity, ice-period support, wind speed limits |
| D3 | Sensor configuration | Available sensor types and quantities, sampling frequency, maximum tolerable failed sensors |
| D4 | Communication state | Network latency upper bound, allowable packet loss rate, minimum bandwidth, OT–IT link availability |
| D5 | Actuator state | Gate/pump availability ratio, response time upper bound, maximum simultaneous failed actuators |
| D6 | Demand and dispatch | Downstream water demand range, dispatch regulation constraints, joint dispatch protocols |

## 7.2   ODD boundary monitoring

The system shall be capable of real-time monitoring of whether current operating conditions are within the ODD. When any dimension parameter is detected to exceed the ODD boundary, the system shall execute the degradation strategy within a specified time. The degradation strategy shall define:

trigger conditions (which parameters exceeding which thresholds);

target degradation level and corresponding MAS control authority changes (e.g., Cloud MAS → Edge MAS → SCADA local control);

degradation transition time window;

control strategy during degradation;

operator alerting method and information content.

## 7.3   ODD expansion and modification

After system commissioning, any ODD expansion (e.g., adding ice-period operation capability, expanding flow range) shall be classified as a Class A change and shall require complete XIL retesting and third-party review before deployment. ODD changes shall produce complete change audit records.

# 8   Multi-network coordinated security

## 8.1   Network zoning

Following the zoning principles of IEC 62443, the water network shall be divided into the security zones specified in Table 4, with MAS component deployment rules defined for each zone.

Table 4 — Network security zone definitions and MAS deployment rules

| Zone | Name | Deployed components | Security requirements |
| --- | --- | --- | --- |
| Zone 0/1 | Field control zone | PLCs, sensors, RTUs | MAS shall not directly access this zone; all access shall be through SCADA gateways |
| Zone 2 | Process monitoring zone (OT network) | Edge agents, Area agents | Fibre-optic ring network, physically isolated, internet connection strictly prohibited. Carries MAS–SCADA command exchange and inter-agent DMPC negotiation |
| Zone 3 | Production management zone (DMZ) | Data gateways, isolation devices | Security filtering and audit for cross-network data exchange |
| Zone 4 | Enterprise zone (IT network) | Cloud agents, digital twin platform | May connect to internet. Carries global dispatch optimization and external data acquisition |

## 8.2   Cross-network data exchange

### 8.2.1   Data uplink (OT → IT): State snapshot push

Edge agents shall serialize real-time operational state (state vectors) into standard formats (JSON/Protobuf) and transmit them via reverse isolation devices (unidirectional data diodes) to cloud agents. Uplink data shall include timestamps, data quality flags, and source identifiers.

### 8.2.2   Command downlink (IT → OT): Dispatch recommendation mechanism

Cloud agents shall not issue direct control commands. Cloud MAS shall only issue “dispatch recommendations” (reference trajectories) or “macro objectives” (goals). A security gateway at the OT network boundary shall process these as follows:

receive the dispatch recommendation from the cloud;

verify the digital signature;

perform ODD boundary secondary validation (verify that recommendation parameters are within the ODD-permitted range);

upon successful validation, forward to the edge agent, which converts recommendations into specific control commands.

Core principle: Control authority shall always reside on the OT side (edge); the cloud shall provide recommendations only.

## 8.3   Disconnection autonomy capability

When the communication link between the OT and IT networks is interrupted (Zone 2–Zone 4 disconnection), edge agents shall detect the disconnection within 1 second and automatically switch to island autonomy mode:

edge agents shall cease waiting for cloud instructions and autonomously maintain operations based on local objectives and local sensor data;

if the internal OT fibre-optic network remains operational, edge agents shall continue distributed coordinated control via DDS;

the system shall log the operational state at the moment of disconnection and subsequent control decision records for synchronization after communication restoration;

upon communication restoration, the system shall automatically perform state alignment and parameter synchronization for a smooth transition back to normal coordinated mode.

## 8.4   Cybersecurity requirements

Cybersecurity of the water network intelligent control system shall comply with IEC 62443. The OT control network and the IT enterprise network shall be physically or logically isolated. Remote access shall employ encrypted communications and multi-factor authentication. OTA update channels shall have independent security verification mechanisms.

# 9   Water network common information model (Water-CIM)

## 9.1   Architecture

Water-CIM shall adopt a package-based structure inspired by the IEC 61970 CIM layered architecture, reconstructed for water network characteristics. To support the SCADA+MAS integration architecture, an Agent Package and a Control Package are added as core increments beyond power-sector CIM. The six-package structure is specified in Table 5.

Table 5 — Water-CIM package structure

| Package | Name | Description and core elements |
| --- | --- | --- |
| P01 | Core | Base package defining IdentifiedObject base class (mRID[UUID], name, aliasName, description) for global unique identification and administrative code mapping |
| P02 | Topology | Defines ConnectivityNode, Terminal, and connection relationships. Supports automatic adjacency matrix generation via graph search |
| P03 | Asset | Defines Gate, Pump, Reservoir, Channel, Pipeline and other hydraulic assets with physical parameters |
| P04 | Measurement | References OGC WaterML 2.0 for time-series encoding and OGC SensorThings API for sensor access |
| P05 | Control | Core increment: defines ControlMode (L0–L5), HardConstraint, SoftConstraint, ODD, FallbackStrategy objects |
| P06 | Agent | Core increment: defines AgentID, AgentType (Edge/Area/Cloud), Zone, ControlAuthority, HeartbeatConfig for MAS semantic objects |

## 9.2   Agent Package requirements

Each agent instance shall be registered as an Agent object in Water-CIM with the following mandatory attributes:

AgentID: globally unique identifier (UUID);

AgentType: enumeration taking one of Edge, Area, or Cloud;

Zone: the network security zone in which the agent is deployed (Zone 2 or Zone 4);

ControlAuthority: current control authority assignment (local manual / edge automatic / cloud advisory);

HeartbeatConfig: heartbeat configuration including period, timeout threshold, and degradation target upon timeout;

ManagedAssets: list of assets under the agent’s jurisdiction (referencing Asset Package objects);

LocalTopology: identifier of the local topology subgraph loaded by the agent.

## 9.3   Control Package requirements

HardConstraint objects shall include the constraint variable identifier, upper/lower bounds, and the response action upon violation (e.g., trigger circuit breaker, emergency shutdown). SoftConstraint objects shall include the target variable, target value, weight, and allowable deviation range. Formalizing safety boundaries as model objects enables MBD compilers to automatically generate underlying safety verification code.

## 9.4   SCADA tags semantic mapping

At engineering delivery, a machine-readable mapping table from SCADA tags to Water-CIM objects shall be provided (e.g., Register_4001 → Gate.Opening). The mapping table shall be delivered in a standard format (CSV or JSON) and shall be subject to version management.

## 9.5   Data exchange format

Water-CIM XML exchange shall use RDF/XML encoding with the namespace prefix “wcim”. For RESTful API scenarios, an equivalent JSON-LD encoding shall be provided. Time-series data shall be compatible with OGC WaterML 2.0 JSON encoding. Sensor access shall be compatible with OGC SensorThings API.

# 10   Interoperability protocol stack

Under the SCADA+MAS integration architecture, a strict distinction shall be made between “computation standards” and “communication standards.” OpenMI/FMI are model computation interfaces, not network protocols, and shall not be used for distributed communication. This clause defines the applicable scope of three protocol layers, as specified in Table 6.

Table 6 — Interoperability protocol stack

| Protocol layer | Standard | Applicable scope | Typical scenario |
| --- | --- | --- | --- |
| Computation kernel (how to compute) | FMI 3.0 / OpenMI 2.0 | Intra-agent model coupling | MPC algorithm calling hydraulic FMU for water level prediction — in-memory high-frequency calls |
| Distributed bus (how to connect) | DDS (OMG standard) | Inter-agent real-time coordination | Upstream agent notifying downstream agent of flow changes — millisecond-level fibre-optic communication |
| Device interface (how to ground) | OPC UA (IEC 62541) | MAS–SCADA interaction | MAS reading gate opening / issuing water level set-points — OT/IT integration bridge |

## 10.1   Computation kernel layer: FMI and OpenMI

### 10.1.1   FMI 3.0 execution container

Model components participating in MPC optimization shall be packaged as FMI 3.0-compliant Functional Mock-up Units (FMUs). Requirements:

support Co-Simulation mode;

implement state save and restore interfaces (fmi3GetFMUState/fmi3SetFMUState) to support multiple forward simulations by MPC optimizers;

provide modelDescription.xml with variable naming compliant with Water-CIM semantics;

declare numerical stability ranges (reasonable value domains for inputs and outputs) for health monitoring.

NOTE   FMI is a computation component interface used within an agent’s process memory. It does not involve network communication.

### 10.1.2   OpenMI 2.0 semantic layer

The OpenMI 2.0 interface definitions (IIdentifiable, ITimeSpaceComponent, IExchangeItem) shall be reused to ensure compatibility with the existing water modelling ecosystem. OpenMI serves as a higher-level cross-physics orchestration standard (e.g., hydrological + hydraulic model coupling).

### 10.1.3   Model health monitoring and version audit

An IHealthMonitor interface shall be implemented (checkState, getQualityFlag, triggerCircuitBreak) along with an IAuditTrail interface (getModelVersion, getVerificationHash, getDeploymentTimestamp) to ensure that model runtime anomalies are detectable and that online model versions are auditable.

## 10.2   Distributed bus layer: DDS

### 10.2.1   Selection rationale

Real-time east–west communication between distributed MAS nodes shall use DDS (Data Distribution Service) as the communication bus. The rationale for selecting DDS:

OpenMI is not applicable: it uses a synchronous blocking call model that cannot handle network latency or disconnection;

MQTT is not applicable: it requires a central broker (single point of failure) and offers insufficient QoS real-time guarantees;

DDS advantages: decentralized (brokerless), peer-to-peer connectivity between nodes, QoS contracts (e.g., DEADLINE of 100 ms). Even if the cloud is down, DDS guarantees continued distributed control as long as the OT fibre-optic links remain operational — natively supporting island autonomy.

### 10.2.2   DDS configuration requirements

DDS Domain allocation: each Area MAS jurisdiction shall be assigned an independent DDS Domain ID;

Topic definition: DDS Topics shall align with Water-CIM semantics (e.g., wcim/Gate/Opening);

QoS configuration: safety-critical messages shall use RELIABLE + DEADLINE policies (default 100 ms threshold); general status messages may use BEST_EFFORT;

Security: DDS Security plugins shall be enabled, supporting authentication, access control, and data encryption.

## 10.3   Device interface layer: OPC UA

North–south communication between MAS and SCADA shall use OPC UA (IEC 62541) as the device interface layer. A companion specification, “Water Network OPC UA Information Model,” shall be developed to establish standard mapping between Water-CIM objects and OPC UA nodes.

## 10.4   Legacy model minimum compliance: BMI

For the large number of legacy Fortran/C++ models existing in water networks, this document establishes BMI (Basic Model Interface) as the minimum compliance threshold for model integration. Any legacy model intended for integration with a water network control platform shall, at minimum, implement BMI’s initialize(), update(), update_until(time), and finalize() standard functions plus necessary input/output variable access interfaces.

# 11   Scenario-based testing and verification

## 11.1   Six-dimensional scenario space

Water network control scenarios shall be defined by six-dimensional parameter combinations, following the ISO 21448 (SOTIF) framework, as specified in Table 7.

Table 7 — Six-dimensional scenario space

| Dim. | Name | Example parameters |
| --- | --- | --- |
| D1 | Topology | Network scale, parallel/series structure, branch count, ring networks, topology changes |
| D2 | Hydraulics | Initial water levels, flow ranges, boundary condition types, water hammer, open-channel unsteady flow |
| D3 | Environment | Rainfall processes, temperature ranges, ice-period conditions, evaporation periods |
| D4 | Perception | Sensor types/accuracy, sampling frequency, single/multiple sensor failures, data drift |
| D5 | Communication | Network latency, packet loss, bandwidth limits, OT–IT link interruption, DDS partition isolation |
| D6 | Fault | Actuator faults, sensor faults, algorithm divergence, MAS crash, multi-type coupled faults |

## 11.2   Scenario classification and priority

Scenarios shall be classified by function (normal dispatch, emergency, degradation, boundary) and by priority:

P0 (mandatory): Safety-critical scenarios involving hard constraints — 100 % coverage required;

P1 (important): Common scenarios covering >90 % of daily operations, including OT–IT disconnection with island autonomy — ≥95 % coverage required;

P2 (recommended): Rare conditions for robustness enhancement — ≥80 % coverage.

## 11.3   XIL testing levels

Table 8 — XIL testing level requirements

| Level | Control algorithm form | Plant form | Verification objective | Acceptance criterion |
| --- | --- | --- | --- | --- |
| MIL | Mathematical model | Mathematical model | Algorithm logic correctness | Zero hard constraint violations; all P0 passed |
| SIL | Auto-generated code | Mathematical model | Code–model consistency | Control output deviation ≤1 % |
| HIL | Real controller + Edge MAS | Real-time simulator + SCADA emulator | Real-time performance, multi-network coordination | Circuit breaker response within spec; disconnection autonomy switch successful |

## 11.4   HIL enhanced requirements

In addition to all SIL requirements, HIL testing shall verify:

SCADA heartbeat circuit breaker: upon injecting an MAS crash fault, SCADA shall revert to local control within 500 ms;

disconnection autonomy switch: after physically severing the Zone 2–Zone 4 link, edge agents shall switch to island autonomy mode within 1 second;

human takeover effectiveness: human takeover initiated at any runtime moment shall result in smooth transition;

multi-fault coupled scenarios (e.g., sensor failure + MAS communication interruption simultaneously);

DDS communication latency and reliability under real OT network conditions.

## 11.5   Coverage requirements

P0 (mandatory): 100 % coverage, all passed;

P1 (important): ≥95 % coverage, ≥98 % pass rate;

P2 (recommended): ≥80 % coverage.

# 12   Engineering acceptance

## 12.1   Acceptance package composition

At engineering acceptance, the constructor shall submit an engineering acceptance package. For the SCADA+MAS integration architecture, the package shall contain the documents specified in Table 9.

Table 9 — Engineering acceptance package composition

| No. | Document | Content requirements |
| --- | --- | --- |
| 1 | ODD declaration | Complete ODD parameter ranges and degradation strategies, including OT–IT disconnection degradation plan |
| 2 | Constraint template | Formalized definitions of all hard/soft constraints using Water-CIM Control Package format |
| 3 | Scenario coverage report | P0/P1/P2 coverage statistics and scenario execution result matrix |
| 4 | XIL test reports | MIL, SIL, HIL phase reports including DDS/OPC UA communication test results |
| 5 | Safety case | Structured safety argument using GSN or CAE framework, covering MAS crash and disconnection scenarios |
| 6 | Model version audit record | Hash comparison proving online model/code matches SIL-verified version |
| 7 | Distributed deployment topology file (DDT) | IaC script describing agent deployment locations, IPs, DDS Domain configuration; shall support one-click deployment and failover migration |
| 8 | Multi-network security policy set | Zone partitioning scheme, isolation device configuration, cross-network rules. Including penetration test report |
| 9 | Disconnection autonomy test report | Test record showing edge agents switching to island autonomy within 1 s after physical network severance |

## 12.2   Acceptance conditions

### 12.2.1   Necessary conditions

Acceptance shall be granted only when all of the following conditions are satisfied:

P0 scenario coverage is 100 %, all passed;

P1 scenario coverage ≥95 %, pass rate ≥98 %;

zero hard constraint violations during HIL testing;

SIL–MIL control output numerical deviation ≤1 %;

SCADA heartbeat circuit breaker test passed: SCADA reverts to local control within 500 ms after MAS failure;

disconnection autonomy test passed: edge agents enter island autonomy within 1 s after OT–IT link interruption;

penetration test passed: no direct access from IT network to MAS nodes on OT network;

safety case passes independent third-party review (L3+) or internal review (L2).

### 12.2.2   Veto conditions

Acceptance shall not be granted if any of the following conditions is present:

P0 scenarios are uncovered or have failed items;

hard constraint violations occurred during HIL testing;

model version audit records cannot be provided, or online version does not match verified version;

safety case is missing or failed review;

disconnection autonomy or SCADA heartbeat circuit breaker tests failed.

## 12.3   Tiered acceptance requirements

Table 10 — Tiered acceptance requirements matrix

| Level | P0 coverage | HIL | Safety case | XIL testing | 3rd-party review | Disconnection autonomy | Penetration test |
| --- | --- | --- | --- | --- | --- | --- | --- |
| L1 | 100 % | Waivable | Simplified | MIL | Waivable | Waivable | Recommended |
| L2 | 100 % | Required | Complete | MIL+SIL+HIL | Recommended | Required | Required |
| L3 | 100 % | Required | Complete | MIL+SIL+HIL | Required | Required | Required |
| L4 | 100 % | Required + extended | Complete + continuous | MIL+SIL+HIL | Required | Required | Required |

# 13   Version management and continuous compliance

## 13.1   Version numbering

Semantic versioning (Major.Minor.Patch) shall be adopted. Each version shall generate a unique SHA-256 strong hash covering model files, auto-generated code, configuration parameters, and MAS deployment configuration.

## 13.2   Change classification

Table 11 — Change classification and control requirements

| Change class | Typical scenarios | Regression testing | Approval requirements |
| --- | --- | --- | --- |
| Class A (major) | ODD expansion, control strategy reconstruction, MAS architecture change | Complete XIL retesting | Third-party review + expert evaluation |
| Class B (general) | Algorithm optimization, new features, DDS QoS policy adjustment | Affected scenarios + full P0 | Internal approval |
| Class C (minor) | Parameter adjustment, bug fixes, agent configuration fine-tuning | Full P0 + affected scenarios | Internal approval |

## 13.3   OTA update process

Over-the-air algorithm updates shall follow this process:

Change request: submit change reason, impact analysis, and change classification;

Regression testing: execute testing appropriate to the change classification;

Approval and release: test reports shall be approved before release;

Canary deployment: the new version shall first operate in “shadow mode” (no actual control authority, compute-and-compare only). For MAS updates, per-agent canary deployment shall be supported rather than network-wide simultaneous switchover;

Post-release monitoring: continuously monitor system behaviour differences after release; support rapid rollback to the previous version upon anomaly detection.

## 13.4   Audit and traceability

A complete change audit chain shall be established, including: change request forms, regression test reports, approval records, deployment records (including old/new version hash comparison and MAS deployment topology change records), and post-release monitoring reports. The online system shall periodically auto-verify that running code hashes match audit records. All audit records shall be retained for at least 5 years after system decommissioning.

## 13.5   Continuous compliance mechanism

Engineering acceptance is not a one-time event. After system commissioning, a continuous compliance mechanism shall be established to ensure that any algorithm update, model upgrade, or MAS architecture adjustment undergoes sufficient verification. The constructor shall designate a dedicated version management officer responsible for full-process change control.

# Annex A (informative)

## Comparison with SAE J3016 driving automation levels

Table A.1 — Water network autonomy levels vs. SAE J3016 comparison

| Level | Water network | SAE J3016 | Key differences |
| --- | --- | --- | --- |
| L0 | Manual operation | No Driving Automation | Essentially equivalent |
| L1 | Assisted operation | Driver Assistance | Water: Cloud MAS advisory; Auto: steering/acceleration assistance |
| L2 | Partial automation | Partial Driving Automation | Water: longer control cycles (minutes–hours), requires SCADA layer execution |
| L3 | Conditional autonomy | Conditional Driving Automation | Critical watershed for responsibility transfer. Water: wider takeover window, but OT/IT separation adds architectural complexity |
| L4 | High autonomy | High Driving Automation | Water: more complex ODD (multi-scale, multi-objective, social factors) |
| L5 | Full autonomy | Full Driving Automation | Both are long-term vision goals |

Water network systems exhibit greater inertia (slower water flow changes), wider fault tolerance time windows (minutes to hours), but higher coupling complexity (multi-scale, multi-objective, with social factor involvement) compared to automotive systems. Furthermore, water networks must achieve distributed coordination under the constraint of physical OT/IT isolation. Therefore, while the water network classification borrows the SAE J3016 framework, it reconstructs ODD definitions, SCADA+MAS architecture requirements, multi-network security, and acceptance criteria specifically for water sector characteristics.

# Annex B (informative)

## Protocol selection decision matrix

Table B.1 provides guidance for engineering designers to quickly determine which interoperability standard to apply for a given integration scenario.

Table B.1 — Protocol selection decision matrix

| Scenario | Recommended protocol | Rationale |
| --- | --- | --- |
| Agent-internal MPC calling hydraulic model for prediction | FMI 3.0 | In-process memory-level calls; state rollback needed for multiple forward simulations |
| Agent-internal cross-physics orchestration (hydrology + hydraulics) | OpenMI 2.0 | Semantic-layer standard for cross-physics component orchestration |
| Upstream agent notifying downstream agent of flow change | DDS | East–west distributed real-time communication; decentralized; supports island autonomy |
| Edge MAS reading real-time gate opening from SCADA | OPC UA | North–south device interface; OT/IT integration bridge; semantic mapping |
| Edge MAS issuing water level set-point to SCADA | OPC UA | Set-point driven paradigm; MAS does not directly operate DOs |
| Cloud MAS issuing dispatch recommendation to Edge MAS | Cross-network security channel | IT→OT unidirectional penetration; requires signature verification + ODD secondary validation |
| Legacy Fortran model integration to platform | BMI | Minimum compliance threshold; implement 4 standard functions |

# Bibliography

[1]  ISO 19156, Geographic information — Observations, measurements, and samples

[2]  OGC SensorThings API, Part 1: Sensing, Version 1.1

[3]  OpenGMS-IS, Open Geographic Modelling and Simulation — Integration Specification

[4]  CSEF BMI, Basic Model Interface, Community Surface Dynamics Modeling System

[5]  IEC 61131-3:2013, Programmable controllers — Part 3: Programming languages

[6]  IEEE 2030.5, IEEE Standard for Smart Energy Profile Application Protocol

[7]  ISO 19440, Enterprise integration — Constructs for enterprise modelling

[8]  NIST SP 800-82 Rev. 3, Guide to Operational Technology (OT) Security

[9]  SAE J3016:2021, Taxonomy and Definitions for Terms Related to Driving Automation Systems for On-Road Motor Vehicles

[10] ISO/TR 4804, Road vehicles — Safety and cybersecurity for automated driving systems — Design, verification and validation